Faculty of Applied Sciences
Bachelor of Science in Computing / Artificial Intelligence

COMP4299/CSAI4299 Final Year Project
Progress Report

Academic Year 2026/27

| An IoT Environmental Monitoring System with Real-Time Alerting and Spark-Based Distributed Batch Analytics for Server Rooms |  |
| --- | --- |
| Project number: | 81 |
| Student ID: | P2321251 |
| Student name: | Sun WenBin |
| Supervisor: | Tang Su Kit Jacky |
| Assessor: | Your assessor |
| Submission Date: | XXX XX, 2026 |

Table of Contents

1	Introduction	5

1.1	Societal, User and Business Needs	6

1.2	Objectives	7

1.3	Ethical Consideration	8

1.4	Summary	9

2	Background and Related Works	10

2.1	Environmental Background	10

2.2	Sensing Technology	10

2.3	Related Work	11

2.4	Summary	12

3	Project Management and Risk Management	13

3.1	Project Time Management	13

3.2	Project Risk Management	15

3.3	Monthly Status Review	18

4	Completed Work	19

4.1 System Overview and Architecture	19

4.2 Sensing and Data Ingestion	19

4.3 Dashboard and Alerting	20

4.4 Spark and Hive Batch Layer	20

4.5 System Verification	21

4.6 Difficulties Encountered and Solutions Adopted	22

5	Conclusion	23

References	24

Appendix A. Ethics Checklist	25

Appendix B. Declaration of the Use of Generative AI in FYP	28

Table of Figures

Figure 1: Activity List	13

Figure 2: Precedence Diagramming Method Diagram	14

Figure 3: Gantt Chart	14

Figure 4: Probability impact matrix before proposed solution	16

List of Tables

Table 1: Comparison of monitoring approaches for small server rooms	10

Table 2: Table of prioritized risk	16

Table 3: Verification of the measurable objectives against the running system	20

# Introduction

Modern organisations depend on computing infrastructure whose reliability is tightly coupled to the ambient environment. Server rooms and small data centres house servers, network equipment and storage that are sensitive to temperature and humidity; ASHRAE TC 9.9 thermal guidelines recommend keeping such rooms within a defined operating envelope, because prolonged exposure to heat accelerates component ageing and shortens hardware life.

Small server rooms — for example those in universities, clinics, retail banks and small enterprises — rarely justify the cost of a commercial building management system or data-centre infrastructure management platform, and their environmental conditions are often checked manually or not at all. Because a temperature or humidity excursion can silently damage equipment before an operator notices, heat- and moisture-related failures are among the most common causes of hardware loss in such rooms, and the resulting unplanned downtime is expensive.

Recent advances in the Internet of Things (IoT) and low-cost embedded sensing make it feasible to build such protection for a fraction of the cost of commercial systems. This project therefore designs and implements a low-cost IoT-based environmental monitoring system that continuously measures the temperature and humidity of a server room, displays the readings on a real-time web dashboard, notifies the operator through Telegram when configurable thresholds are exceeded, and keeps the data for long-term query, export and analysis. In short, the project problem is: how to build a low-cost, reliable and easy-to-operate system that keeps server-room temperature and humidity under continuous observation, alerts the operator promptly, and preserves a useful historical record.

Continuous environmental monitoring is not a new problem, and the work of others falls into three strands. At the guideline level, ASHRAE TC 9.9 publishes thermal specifications that define the recommended operating ranges for computing equipment; these values now underpin the thresholds used by most monitoring systems, including the present one. At the commercial level, building management systems and data-centre infrastructure management (DCIM) platforms provide comprehensive, site-wide monitoring, but they are costly to purchase and license and are largely closed systems — out of reach of the small server rooms this project targets. At the research and open-source level, the IoT literature (e.g. Gubbi et al.) has shown how cheap, networked sensors can be deployed to gather environmental data, and lightweight web back-ends built with Flask together with embedded storage such as SQLite are well-proven ways to collect and serve small telemetry streams.

Each of these strands is directly applicable to the present problem: ASHRAE supplies the threshold values, the IoT approach supplies the sensing architecture, and the Flask/SQLite stack supplies a known-good data path, so the building blocks do not need to be re-invented. Where existing work falls short is in integration and focus. Commercial platforms are too expensive and too closed for a small facility, while most research demonstrations stop at collecting and plotting data — they lack practical alerting, an operator-facing dashboard, and long-term retention with export, which are precisely what a busy non-specialist operator needs. This project differs by combining the proven elements — Raspberry Pi sensing, immediate Telegram alerting, a real-time web dashboard, persistent storage with CSV export, and a Spark/Hive layer for historical analysis — into a single affordable system aimed at small server rooms. Because earlier demonstrations concentrated on proving the sensing technology, whereas this work concentrates on dependable, day-to-day operation and usefulness to the operator, this integration-focused approach is expected to produce a more practical outcome. A detailed comparison of related systems is given in Chapter 2.

The main technical challenges are: (i) sensor reliability, since the digital sensor occasionally returns invalid readings that must be detected and retried; (ii) achieving a capture rate of at least 99% over an imperfect network, handled by buffering readings locally on the sensor node and retransmitting them when connectivity recovers; (iii) meeting responsiveness targets of sub-2-second dashboard refresh, sub-10-second alert delivery and sub-1-second queries over any 30-day window; and (iv) keeping deployment simple enough for a non-specialist operator. These challenges and the progress made against them in the design and implementation phases are reported in Chapter 4.

## Societal, User and Business Needs

Continuous environmental monitoring addresses needs across several levels of society and of the organisations that operate server rooms.

Societal and environmental needs. By detecting abnormal temperature or humidity before it damages equipment, the system helps prevent premature hardware failure and the associated electronic waste. Because the design uses low-cost, widely available IoT components, meaningful environmental protection becomes affordable for small organisations and institutions that cannot pay for commercial platforms. The system also supports sustainable, energy-conscious operation by helping operators keep cooling within recommended ranges rather than overcooling.

User needs. The day-to-day users are server-room operators, who are not necessarily trained engineers. They need an interface that is simple to read at a glance: a live dashboard showing current temperature and humidity with an intuitive design, and alerts that reach them immediately on a phone. The system is designed to be low-maintenance — sensor nodes are plug-and-play and require no programming to operate — and it notifies the operator again when a condition returns to normal, so that no one is left guessing whether the risk has passed.

Business needs. For the organisation, the primary needs are protecting expensive IT assets and avoiding unplanned downtime, both of which are served by continuous monitoring with prompt alerting. Stored readings also support troubleshooting and reporting — for example, demonstrating that the room was kept within the recommended ASHRAE operating range — and the CSV export function allows the data to be analysed with external tools. Alerts are delivered through the widely used Telegram messenger, avoiding the cost and complexity of proprietary notification infrastructure.

Regulatory and safety considerations. The system processes no personal data, so its data-protection burden is minimal. It operates at low voltage inside a server room, posing no special risk to users or the environment. Rather than imposing new obligations, the system helps the organisation stay within widely accepted thermal operating guidelines for computing equipment. The associated ethics checklist is provided in Appendix A.

## Objectives

The overall aim of this project is a low-cost IoT-based environmental monitoring system for small server rooms, as described in Section 1.1. To turn this aim into an achievable, verifiable deliverable, the project is broken down into the following objectives, each stated in a Specific, Measurable, Achievable, Relevant and Time-bound (SMART) form. Together they are the building blocks of the project: they define what must be built, how well it must perform, and how each performance claim will be evidenced at the end of the project

Objective 1 — Sensor data collection. Continuously read temperature and humidity from two DHT22 sensors mounted on Raspberry Pi nodes at one-minute intervals, with a data capture rate of at least 99% under normal operating conditions. Each sensor reports both temperature (±0.5 °C accuracy) and relative humidity (±2 % RH accuracy), so the system always has a paired temperature–humidity reading for the monitored room. This objective is achieved when readings from every sensor appear in the central database on schedule, and it is verified by comparing the number of stored readings against the number expected over a 30-day run

Objective 2 — Real-time web dashboard. Build an interactive dashboard that shows the current temperature and humidity, together with 24-hour trend charts, and that refreshes in under 2 seconds. This objective is achieved when an operator can open the dashboard and read the current state of the room at a glance, and it is verified by timing a full page refresh while new readings are arriving.

Objective 3 — Threshold alerting. Detect when the temperature or humidity exceeds configurable thresholds and notify the operator through Telegram within 10 seconds of a threshold crossing, while avoiding repeated, flooding messages for the same condition. This objective is achieved when a deliberately induced excursion produces a Telegram message on a phone within the stated time, and a recovery message when the condition returns to normal.

Objective 4 — Data persistence. Store every reading in a time-series database so that any 30-day window of history can be queried in under 1 second. This objective is achieved when the database retains a full, continuous history and long-range queries return promptly; it is verified by timing queries against accumulated data and by inspecting the stored record after an outage-and-recovery test.

Objective 5 — Historical export and analysis. Support export of the stored history as CSV for any requested date range, with a 30-day export completing within 5 seconds, and provide a batch analysis path so that historical readings can be aggregated and examined beyond the real-time dashboard. This objective is achieved when an operator can download a month of data quickly, and it is verified by timing the export and by running the aggregation job over the accumulated dataset.

## Ethical Consideration

At the outset of the project, potential ethical issues were evaluated against the ethics checklist provided in Appendix A. The assessment concluded that no significant ethical issues arise from this project, for the following reasons.

The system monitors only physical environmental variables — the temperature and humidity of a server room. It involves no human participants, so questions concerning consent, vulnerability, withdrawal and participant harm do not apply. It generates and stores no personal or personally identifiable data: the readings are numeric environmental measurements from sensors, identified only by a sensor identifier and a timestamp, with no link to any individual. The project therefore has no data-protection obligations beyond keeping the monitoring database and logs private and protected from unauthorised access, which is handled by restricting the system to the operator's own local network.

The hardware involved operates at low voltage within a server room and exposes the researcher to no risk greater than ordinary study or working life. No illegal or otherwise restricted activities are involved.

## Summary

This report presents the progress of the Final Year Project — a low-cost IoT-based environmental monitoring system for small server rooms — and is organised so that each chapter builds on the one before it, moving from why the project exists, to how it is planned, to what has been achieved so far.

Chapter 1 opens the argument. It first establishes that small server rooms need continuous temperature and humidity monitoring and that existing solutions are too costly or too limited, then states the aim and the five SMART objectives that give the project a measurable target. The societal, user and business needs that the system must serve are set out, and the ethics checklist in Appendix A confirms that the work raises no significant ethical concerns. In short, this chapter answers the question "what are we building, and why is it worth building?" — and the rest of the report shows how that question is being answered.

Chapter 2 supplies the knowledge the reader needs to judge the design that follows: the environmental guidelines for computing equipment, the sensing and IoT technology available, and the monitoring approaches others have taken. Where Chapter 1 argues at a high level that existing work falls short, Chapter 2 examines it in enough detail to justify which building blocks this project adopts and why.

Chapter 3 turns the goal into an executable plan. Because a project that is not managed is a project that drifts, this chapter defines the activities, their dependencies and the schedule, identifies the risks that could threaten the scope, schedule and quality of the work, and assigns each risk a response. The monthly status review then tracks whether the plan is being followed.

Chapter 4 reports what has actually been built, and is where the reader sees the design decisions in action. It walks through the system analysis and architecture — the choice of hardware, the data model, and the sensing, storage, dashboard, alerting and analysis layers — and honestly reports the difficulties encountered and the solutions adopted, so that the reader understands not only what the system does but how and why it came to look this way.

Chapter 5 closes the loop. It compares the completed work against the objectives set in Chapter 1, reflects on what the project has achieved so far, and explains what remains to be done — giving the reader a clear picture of where the project stands and where it is heading.

The report ends with the references used throughout and two appendices: the completed ethics checklist (Appendix A) and the declaration of the use of generative AI (Appendix B).

# Background and Related Works

This chapter provides the background a reader needs to understand the design in Chapter 4, and reviews the related work on which this project builds. It first explains the environmental requirements of computing equipment and the sensing technology adopted, then surveys existing monitoring approaches and compares them with the present system in Table 1, and ends with a brief summary of the state of the art.

## Environmental Background

Server rooms and small data centres concentrate heat-generating equipment in a confined space, so their operating environment must be actively controlled. The most widely cited guidance is published by ASHRAE TC 9.9, whose thermal guidelines define recommended and allowable envelopes for temperature and humidity in data processing environments; excursions beyond these envelopes accelerate component ageing and shorten hardware life, and severe cases cause sudden failure. Because the DHT22 sensor used in this project measures temperature with ±0.5 °C accuracy and humidity with ±2 % RH accuracy, its readings are precise enough to check compliance against these envelopes. The alert thresholds configured in the project, for example 15–30 °C and 20–70 % RH by default, are therefore not arbitrary: they sit inside the ASHRAE-recommended range and reflect the practical operating limits of a small server room.

## Sensing Technology

The Internet of Things has made low-cost environmental sensing widely accessible. A sensing node of this kind typically couples an inexpensive computing platform with commodity digital sensors and forwards measurements over a network. The Raspberry Pi is well suited to this role: it runs a full Linux system, provides general-purpose input/output (GPIO) pins, and can therefore drive sensors and transmit readings using ordinary networking and scripting tools. The DHT22 (also sold as the AM2302) is a digital temperature-and-humidity sensor that communicates over a single data wire; its datasheet specifies the accuracy and timing the sensor is expected to meet, and only one GPIO pin is needed per sensor. A practical caveat is that the DHT22 is timing-sensitive and occasionally returns invalid reads, which the collection software must detect and retry — a point that directly influences the data-quality measures described in Chapter 4.

## Related Work

Continuous environmental monitoring for computing facilities is well established, and existing approaches fall into three broad groups. At the commercial level, building management systems and data-centre infrastructure management (DCIM) platforms provide accurate, multi-point, site-wide sensing with professional alarm and reporting features; however, they are expensive to purchase and licence and are largely closed systems, which places them out of reach of small and medium-sized organisations. At the open-hardware level, many projects combine a Raspberry Pi with a DHT22 to log temperature and humidity, and the IoT literature, for example Gubbi et al., provides the underlying design vocabulary of low-power devices collecting and forwarding physical measurements. Such projects demonstrate that low-cost sensing works, but they usually stop at logging and plotting data. On the software side, lightweight REST back-ends built with Flask, embedded relational storage such as SQLite, browser-rendered charts via Chart.js and instant notifications through the Telegram Bot API are all well-proven building blocks for small telemetry services, each adding little overhead while providing fast, indexed queries and low-latency delivery.

To make the positioning concrete, Table 1 compares the three representative options that a small organisation might consider, across the dimensions that matter for day-to-day monitoring.

Table 1: Comparison of monitoring approaches for small server rooms

| Dimension | Commercial BMS/DCIM | Open-hardware IoT logging | This project |
| --- | --- | --- | --- |
| Target setting | Large data centres / whole buildings | Demonstrations and learning | Small server rooms |
| Cost | High (purchase and licence) | Low | Low |
| Sensing | Multi-point, professional grade | Single DHT22 node | Two DHT22 nodes |
| Real-time alerting | Yes (proprietary console) | Usually none | Telegram, within 10 s |
| Operator interface | Professional control console | Simple charts | Web dashboard (<2 s refresh) |
| History and export | Commercial reporting suite | Local files only | SQLite 30-day query <1 s, CSV export |
| Long-term analysis | Built-in | None | Spark/Hive batch layer |

Table 1 summarises the contrast. Commercial platforms are feature-complete but costly and closed; open-hardware logging projects are cheap but stop at data capture and plotting; this project combines the two, adding practical alerting, an operator dashboard, durable storage with export, and a batch-analysis layer, at a cost comparable to the open-hardware option. The gap that motivates this project is therefore one of integration and operation, not of any single component: no existing option ties these proven elements together behind measurable service targets — a capture rate of at least 99 %, sub-2-second dashboard refresh, sub-10-second alert delivery and sub-1-second queries over any 30-day window — at a price a small organisation can afford. This project addresses that gap by combining the proven elements into one low-cost system and validating the whole against these targets in a server-room scenario. For longer-term analysis it additionally includes a batch-processing path built on Apache Spark with the Hive warehouse, which aggregates large histories of readings efficiently — the area in which this work goes beyond a typical single-board logging project.

## Summary

In short, the components used by this project are individually mature and well documented; the contribution lies in their careful integration into an affordable, maintainable system, and in the quantitative validation of that integration against the objectives set out in Chapter 1. The detailed design decisions that follow from this position are presented in Chapter 4.

# Project Management and Risk Management

A project of this kind succeeds not only through technical work but through careful planning, scheduling and control. This chapter describes how the Final Year Project is planned, managed and kept on course towards the objectives set out in Chapter 1. Section 3.1 presents the time management of the project: the activity list that decomposes the whole project into identifiable tasks, the precedence diagram that shows the dependencies between them and highlights the critical path, and the Gantt chart that maps the work onto the academic calendar. Section 3.2 assesses the risks that could threaten the project's scope, schedule and quality, ranks them by priority and describes the responses adopted to mitigate them, showing how the plan is made robust to foreseeable problems. Section 3.3 reports the monthly status review, which tracks what has been accomplished in each period and what is planned for the coming month. In short, this chapter explains not only what the project aims to deliver — that was established in Chapter 1 — but how the delivery is organised and protected against the risks identified during planning.

## Project Time Management

| Activity | Description | Duration | Predecessor |
| --- | --- | --- | --- |
| A1 | Literature review and requirements analysis | 3 wks (W1-3) | - |
| A2 | Project planning; write Chapter 3 of Progress Report | 1 wk (W5) | A1 |
| A3 | Proposal and ethics form submission | 2 wks (by 10 Sep) | A1 |
| A4 | Hardware setup: Raspberry Pi + DHT22, sensor script and calibration | 4 wks (W6-9) | A1, A3 |
| A5 | Backend development: Flask ingestion API, SQLite persistence, threshold checking, Telegram alerts | 4 wks (W9-12) | A4 |
| A6 | Progress Report submission and presentation | 2 wks (W12-13) | A2, A5 |
| A7 | Dashboard development: Chart.js real-time gauges, 24-hour trends, CSV export | 2 wks (W14-15) | A5 |
| A8 | Address supervisor/assessor comments on Progress Report | 1 wk (W15) | A6 |
| A9 | System integration, 7-day continuous test, SMART-objective validation | 6 wks (S2 W1-6) | A7 |
| A10 | Spark/Hive batch layer (extension): Hive tables, PySpark aggregation job | 3 wks (S2 W3-5) | A7, A8 |
| A11 | Final Report draft submission | 2 wks (S2 W8) | A9, A10 |
| A12 | Poster submission; Final Presentation and Poster Presentation | 2 wks (S2 W9-10) | A11 |
| A13 | Revise Final Report based on presentation feedback; prepare demo video | 2 wks (S2 W11-12) | A12 |
| A14 | Final Report submission, demo video submission, and optional conference-ready manuscript | 1 wk (S2 W13) | A13 |

Figure 1: Activity List

Figure 2: Precedence Diagramming Method Diagram

Figure 3: Gantt Chart

## Project Risk Management

Risk 1: Invalid or inaccurate DHT22 readings

- Description: The DHT22 occasionally returns out-of-range or spurious values. Such readings would corrupt the dataset and could break the accuracy (±0.5 °C, ±2 % RH) and capture-rate (≥99 %) objectives.

- Probability of occurrence: medium

- Impact: Medium. It corrupts data quality and threatens the verification targets.

- Response: Validate and retry each read, reject out-of-range values in the collection script, cross-check readings across multiple sensors, and calibrate against a reference thermometer and hygrometer.

Risk 2: Unstable network link between the Raspberry Pi and the server

- Description: Readings are transmitted from the Raspberry Pi to the central server over the local network. Intermittent connectivity drops readings and directly threatens the ≥99 % capture-rate target.

- Probability of occurrence: medium

- Impact: High. A single network outage window directly violates the primary capture-rate objective.

- Response: Buffer readings locally on the Raspberry Pi and re-transmit them when connectivity recovers; keep a local CSV copy as a fallback.

Risk 3: Alert delivery delay or failure

- Description: Threshold alerts are delivered through the Telegram Bot API. API unavailability or network delays could prevent the 10-second alert target from being met.

- Probability of occurrence: low

- Impact: Medium. Delayed alerts reduce the usefulness of the monitoring system but do not affect data collection.

- Response: Evaluate thresholds at the point of ingestion, retry sending with backoff, and use SMTP email as a secondary notification channel.

Risk 4: Server downtime or SQLite data corruption

- Description: The server runs on a single virtual machine. A crash or database corruption would lose the stored history and break the query and export functions.

- Probability of occurrence: low

- Impact: High. Losing all stored readings undermines the data-persistence and reporting objectives.

- Response: Enable SQLite WAL mode, schedule regular database backups, and retain the appended CSV as a secondary record.

Risk 5: Query or export performance targets missed

- Description: Large date-range queries on the readings table could exceed the 1-second query and 5-second export limits.

- Probability of occurrence: low

- Impact: Medium. It fails the performance objectives but does not stop the system from functioning.

- Response: Index the timestamp column, pre-aggregate data, and paginate large exports.

Table 2: Table of prioritized risk

| Priority | Risk Identifier and Description |
| --- | --- |
| 1 | Risk 2: Unstable network link between the Raspberry Pi and the server |
| 2 | Risk 4: Server downtime or SQLite data corruption |
| 3 | Risk 1: Invalid or inaccurate DHT22 readings |
| 4 | Risk 3: Alert delivery delay or failure |
| 5 | Risk 5: Query or export performance targets missed |

| Probability | High |  |  |  |
| --- | --- | --- | --- | --- |
|  | Medium |  |  |  |
|  | Low | Risk 3 Risk 4 Risk 5 | Risk 1 Risk 2 |  |
|  |  | Low | Medium | High |
|  |  | Impact |  |  |

Figure 4: Probability impact matrix before proposed solution

## Monthly Status Review

Attach the monthly status review of your project here. You have to briefly report what tasks you have accomplished and your plan for the coming month.

# Completed Work

This chapter reports the work completed so far. It is organised to follow the flow of data through the system, from the sensor to the analysed result. Section 4.1 gives an overview of the system architecture and the design decisions behind it. Sections 4.2 to 4.4 then describe each layer of the implementation in turn: sensing and data ingestion, the dashboard and alerting, and the Spark and Hive batch layer. Section 4.5 evaluates the system against the measurable objectives set out in Chapter 1, and Section 4.6 records the difficulties encountered and the solutions adopted. Organising the chapter in this way keeps the description close to how the system actually operates, and places the verification of the objectives immediately after the implementation on which it depends.

## 4.1 System Overview and Architecture

This chapter describes the work completed so far. The system has been implemented end to end and is running on real hardware, following the architecture established in Chapter 2 and the plan in Chapter 3. The design separates a lightweight sensing node from a central server: the Raspberry Pi only reads sensors and forwards readings, while the server performs storage, alerting, presentation and analysis.

Two DHT22 sensors are connected to a single Raspberry Pi node on GPIO4 and GPIO17, powered from the 3.3 V rail. Because each DHT22 requires only one GPIO pin, one Raspberry Pi can drive several sensors; mounting both on a single node reduces hardware cost and simplifies deployment while still providing two independent measurement pointsThe node reads both sensors every 60 seconds and posts each reading over the local network to a Flask application on the server. The server validates and stores each reading in a SQLite database, appends it to a CSV file, evaluates it against the configured thresholds, and serves a web dashboard and alert notifications. A separate batch layer, built with Spark and Hive, processes the accumulated readings for longer-term analysis.

## 4.2 Sensing and Data Ingestion

Sensing. The collector script on the Raspberry Pi reads both sensors in each cycle. Because the DHT22 is timing-sensitive and occasionally returns invalid values, each read is retried and discarded if it is still invalid, so that a bad read never enters the dataset. If the network or server is unreachable, readings are written to a local buffer file on the Pi and re-transmitted automatically once connectivity returns. This mechanism protects the capture-rate objective against network outages.

Ingestion. The Flask back end exposes a single ingestion endpoint. Each reading is validated (sensor identifier, numeric temperature and humidity), given a UTC timestamp, and then written to three places: the SQLite database, the rolling CSV file, and the threshold evaluator. The database uses write-ahead logging (WAL) mode together with indexes on the timestamp column and on the (sensor, timestamp) pair, which supports fast range queries over the accumulated history.

Sensor readings can be biased, so the back end supports per-sensor calibration offsets. Each sensor can be given a temperature and a humidity offset, which the server adds to every incoming reading before it is stored, so that the database holds corrected values. By default the offsets are zero, leaving all readings unchanged. The offsets are computed by a small tool that averages recent readings, compares them against a reference instrument, and derives the correction automatically. Because no reference instrument was available during this phase, the offsets remain at zero; the mechanism is in place and can be applied without any code change once a reference is available.

The stored history is protected by an automatic backup routine. The server takes a consistent database snapshot at start-up and then every 24 hours, using the SQLite backup API so that the copy remains valid while the server is writing. Each backup also includes the readings and alert CSV files and a CSV export of the alert log, and is stored in a timestamped folder. The most recent fourteen backups are retained and older ones removed automatically, so the data can be recovered after a disk failure or corruption without manual housekeeping.

## 4.3 Dashboard and Alerting

Dashboard. The web dashboard is rendered in the browser with Chart.js. It shows the current temperature and humidity for each sensor with per-sensor radial gauges, a status strip indicating the connection state and sensor count, and a 24-hour trend that overlays both sensors against the configured threshold bands. The page polls the back end every two seconds, and the thresholds can be edited live from the same page without restarting the system. Historical data can be exported as CSV for any date range and sensor.

Alerting. Threshold evaluation happens at the point of ingestion, so an alert is triggered as soon as a reading crosses a limit. Notifications are delivered through the Telegram Bot API from a background thread so that ingestion is never blocked. Two mechanisms keep the operator from being flooded: repeated alerts for the same condition are suppressed for a cooldown window, and a separate recovery message is sent automatically when the condition returns to normal. This behavior was verified on the real hardware: a deliberate excursion produced a Telegram message on the phone, and the recovery notice arrived without intervention. Beyond immediate notification, every threshold crossing and its recovery are recorded: the back end stores them in a dedicated alerts table and appends them to a separate CSV file. This gives an auditable record of when the room left and returned to its safe range, and the dashboard presents the most recent events in an Alert History panel.

## 4.4 Spark and Hive Batch Layer

On top of the real-time pipeline, a batch-analysis layer was built on a single-node Hadoop, Hive and Spark cluster running inside WSL. A PySpark job reads the accumulated CSV, cleans the data (null and out-of-range filtering), computes hourly aggregates — average, maximum and minimum temperature and humidity per sensor — and writes the result to HDFS, where Hive exposes it as an external table.

This layer answers questions the real-time path cannot: how many hours exceeded the safe temperature or humidity range, how the environment trends day by day, whether the capture-rate target was met in each hour (by counting readings per hour), and whether the two sensors agree with each other. The data-source path of the job is configurable through an environment variable, so the same job can be re-pointed at a different dataset without code changes. The alert records are exported alongside the readings, so the batch layer also analyses alerting behaviour — for example how often each condition fired, or which sensor was responsible for the most events.

## 4.5 System Verification

The measurable objectives set out in Chapter 1 were tested against the running system. Measurements were taken on the real database of 23,705 readings, repeating each measurement five to seven times and taking the average.

Table 3: Verification of the measurable objectives against the running system

| Objective | Target | Measured | Result |
| --- | --- | --- | --- |
| Dashboard refresh | < 2 s | 94 ms (worst 560 ms) | Passed |
| Alert delivery | < 10 s | 0.88 s | Passed |
| 30-day query | < 1 s | 125 ms (worst 142 ms) | Passed |
| CSV export (30 days) | < 5 s | 102 ms (worst 152 ms) | Passed |
| Capture rate | >= 99 % | - | Under observation |

The alert-delivery figure was broken down into its two components: the back-end processing of the reading (ingestion and threshold evaluation) took about 49 ms, and the Telegram round trip took about 826 ms. The bottleneck is therefore the external messaging service and the network, not the server logic, which processes each reading almost instantaneously.

The query and export results confirm that the indexing and aggregation decisions described in Section 4.2 were effective: the 30-day query returns in roughly an eighth of its one-second budget, and the export in about a fiftieth of its five-second budget.

The capture-rate objective is being verified separately. Because it is defined over a continuous operating period, it requires an observation window and is still in progress; the hourly counts produced by the batch layer will provide the evidence.

## 4.6 Difficulties Encountered and Solutions Adopted

Several non-trivial difficulties arose during implementation, and the alternatives considered are recorded here because the reasoning is part of the engineering work.

- Sensor reliability. The DHT22 intermittently returns invalid reads. Rather than smoothing over them, the system retries each read and rejects values outside a plausible range, so that data quality is preserved rather than silently degraded.

- Unstable network link. A dropped connection would have lost readings and broken the capture-rate target. Readings are therefore buffered locally on the Pi and re-sent on recovery, instead of being discarded.

- Hive and the Java runtime. Hive 4.2.1 would not run under Java 21 — its command-line client requires a newer runtime feature set than the one available. The alternative of patching the client was rejected in favour of running Hive on Java 17, which it officially supports, while leaving the rest of the stack unchanged.

- Execution engine. Hive defaulted to the Tez engine, which is not installed, so every query failed with a class-not-found error. The engine was switched to MapReduce, which ships with Hadoop and requires no additional software.

- Process lifetime under WSL. Background Hadoop and Hive services were being terminated whenever the invoking command returned, because WSL shut the distribution down between calls. The whole pipeline was therefore consolidated into a single script that starts the services and runs the job in one invocation.

- Alert flooding. Without suppression, a sustained excursion would have produced a message every minute. A cooldown window was added, together with an automatic recovery notice, so that the operator receives one alert per event rather than a continuous stream.

- Node configuration. The proposal envisaged separate Raspberry Pi nodes, each carrying one DHT22. During implementation the sensors were consolidated onto a single node carrying two sensors. Distributing them across separate nodes was evaluated and rejected, as it would have roughly doubled the hardware cost and the number of devices to maintain; the two independent measurement points that the objective requires are already provided by the single-node arrangement.

# Conclusion

Reflect on the progress of the project. Can use first person pronouns to write. You can reuse the content in the Appendix ‘Reflection’ in the Final Report.

References

[1] Aosong Electronics. AM2302 / DHT22 Digital Temperature and Humidity Sensor Datasheet. Aosong Electronics Co., Ltd., 2012.

[2] Raspberry Pi Foundation. Raspberry Pi Documentation. https://www.raspberrypi.com/documentation/, 2026.

[3] J. Gubbi, R. Buyya, S. Marusic, and M. Palaniswami. Internet of Things (IoT): A vision, architectural elements, and future directions. Future Generation Computer Systems, 29(7):1645–1660, 2013.

[4] ASHRAE TC 9.9. 2011 Thermal Guidelines for Data Processing Environments – Expanded Data Center Classes and Usage Guidance. American Society of Heating, Refrigerating and Air-Conditioning Engineers, Atlanta, GA, 2011.

[5] Chart.js. Chart.js Documentation. https://www.chartjs.org/docs/, 2026.

[6] Telegram Messenger LLP. Bot API. https://core.telegram.org/bots/api, 2026.

[7] Pallets. Flask Documentation. https://flask.palletsprojects.com/, 2026.

[8] SQLite. SQLite Documentation. https://www.sqlite.org/docs.html, 2026.

[9] Apache Software Foundation. Apache Spark Documentation. https://spark.apache.org/docs/latest/, 2026.

[10] Apache Software Foundation. Apache Hive Documentation. https://hive.apache.org/, 2026.

Appendix A. Ethics Checklist

| Name of student: (leader of the team, if applicable) | Sun WenBin |
| --- | --- |
| Student number: | P2321251 |
| Programme: | BSc in Computing BSc in AI MSc in Big Data and IoT PhD in Computer Applied Technology |
| Module: | Final Year Project |
| Title of project: | An IoT Environmental Monitoring System with Real-Time Alerting and Spark-Based Distributed Batch Analytics for Server Rooms |
| Supervisor: | Tang Su Kit Jacky |

Instructions

Answer the following questions honestly. If your answer falls into a shaded box, you must provide additional information on how you will handle the related ethics issues on the last page of this form.

Project summary

This project designs and builds a low-cost, real-time environmental monitoring system for server rooms. Raspberry Pi sensor nodes equipped with DHT22 sensors continuously measure temperature (±0.5 °C accuracy) and humidity (±2 % RH accuracy) at 1-minute intervals and transmit the readings to a central Flask server, where the data is stored in a SQLite database. An interactive web dashboard built with Chart.js and Bootstrap displays real-time gauges and 24-hour trend charts. Configurable threshold alerts send instant Telegram notifications when temperature or humidity exceeds safe limits, and historical data can be exported as CSV for compliance reporting. As an extension, a Spark and Hive batch-processing layer aggregates readings for longer-term trend analysis. The project targets a ≥99 % data capture rate over a 7-day test period, page refresh under 2 seconds, alerts within 10 seconds of a threshold breach, and 30-day queries in under 1 second.

Participants (Consent procedures and possible harm)

|  |  | Yes | No | N/A |
| --- | --- | --- | --- | --- |
| 1 | Does your project include human participants? If no, you can skip the rest of this section. |  | ✓ |  |
| 2 | Will any of the participants be from vulnerable groups, e.g. children under 18, people with communication difficulties, patients in hospital? If yes, please specify: _______________________ |  |  | ✓ |
| 3 | Will you tell participants that their participation is voluntary? |  |  | ✓ |
| 4 | Will you obtain written consent for participation? |  |  | ✓ |
| 5 | Will you tell participants that they may withdraw from the research at any time and for any reasons without penalty? |  |  | ✓ |
| 6 | Is there any realistic risk that any participants could experience either physical or psychological distress or discomfort? |  |  | ✓ |

Data Protection

|  |  | Yes | No | N/A |
| --- | --- | --- | --- | --- |
| 7 | Will any non-anonymised and/or personalized data be generated and/or stored? |  | ✓ |  |
| 8 | Will you have access to documents containing sensitive data about living individuals? |  | ✓ |  |

Researcher Safety

|  |  | Yes | No | N/A |
| --- | --- | --- | --- | --- |
| 9 | Will you be exposed to any risks greater than those encountered in their normal study/working life? E.g. operation of non-standard equipment or extended |  | ✓ |  |
| 10 | Will you be exposed to highly addictive or illegal activities (e.g. gambling, drugs) during the research? |  | ✓ |  |

No ethical issues are identified. The project monitors only physical environmental variables (temperature and humidity) in a server room. It involves no human participants, no personal or anonym sable data, and no activities that pose risks beyond ordinary study or working life.

Any other issues?

Declaration

| Student I have read the instruction carefully and reported honestly the potential ethics issues about the project. ───────────── Date: | Supervisor To the best of my knowledge, the student has reported honestly the potential ethics issues about his/her project. ───────────── Date: |
| --- | --- |

This form is largely based on the ethical approval documents from Cardiff University https://www.cs.cf.ac.uk/ethics/ and University of Glasgow http://www.dcs.gla.ac.uk/ethics/

Appendix B. Declaration of the Use of Generative AI in FYP

Please make sure you understand the policy about using generative AI, and such use must be explicitly acknowledged. The teacher/supervisor responsible for the assessment will provide specific guidance regarding acceptable usage. Failure to follow the rules for your work constitutes academic dishonesty.

| Please tick either one below. ☐ I have used generative AI in this assessment work ☐ I did not use generative AI in this assessment work (please go to sign) |  |
| --- | --- |
| Generative AI tool used (name and version): | ________________________________________________________ |  |

For each relevant area, briefly describe how the information was generated, as well as explain how the output was used in your work. Put N/A if not appropriate.

| Type of usage | GenAI assistance received | Student action on generated content |
| --- | --- | --- |
| Brainstorming and idea generation |  |  |
| Literature review and background research |  |  |
| Data analysis |  |  |
| Programming support |  |  |
| Visualization and diagram production |  |  |
| Text Rewriting and Drafting |  |  |
| Other (please specify): |  |  |

Student signature:
Date: